## Summary
Summary
Total Capital Cost [USD] | 177407000
Total Operating Cost [USD/Year] | 15778700
Total Raw Materials Cost [USD/Year] | 0
Total Product Sales [USD/Year] | 0
Total Utilities Cost [USD/Year] | 9815970
Desired Rate of Return [Percent/'Year] | 20
P.O.Period [Year] | 0
Equipment Cost [USD] | 86874300
Total Installed Cost [USD] | 144315700

## Utilities
Utilities
Name | Fluid | Rate | Rate Units | Cost per Hour | Cost Units
Electricity |  | 2384.223 | KW | 184.7773 | USD/H
Cooling Water | Water | 7.7917 | MMGAL/H | 935.0004 | USD/H

## Unit operation
Unit operation
Name | Equipment Cost [USD] | Installed Cost [USD] | Equipment Weight [LBS] | Installed Weight [LBS] | Utility Cost [USD/HR]
Steam Generator-2 | 3268800 | 6402700 | 910000 | 1612730 | 0
DisCond | 852500 | 1505000 | 249000 | 390226 | 115.2665
1/10th NPP Ref Cond | 43700 | 129500 | 9000 | 23742 | 0
TES Loop cond pump (sized 1/10) | 17500 | 102100 | 1300 | 17739 | 2.3126
TES Pump | 36600 | 247600 | 2400 | 47835 | 0.028675
P-101 | 26700 | 73500 | 1700 | 7740 | 2.8908
NPP Ref Turbine (1/3) | 2800200 | 3134600 | 150200 | 228104 | 0
2ndTurbine-2 | 52600 | 98300 | 3700 | 9658 | 0
NPP Ref Turbine | 0 | 0 | 0 | 0 | 0
Cond-charge cond Pump 1/10 | 17300 | 101900 | 1300 | 17739 | 2.3126
FWH_Mix | 0 | 0 | 0 | 0 | 0
SG | 3187100 | 6320600 | 883000 | 1585594 | 0
FWH Mix | 0 | 0 | 0 | 0 | 0
Discharging Calcs | 0 | 0 | 0 | 0 | 0
Turbine-charge (sized 1/2) | 2325800 | 2613600 | 122500 | 185589 | 0
NPP Ref Condenser | 0 | 0 | 0 | 0 | 270.2645
FWH Split | 0 | 0 | 0 | 0 | 0
TES Pump-2 | 8000 | 54400 | 660 | 7266 | 1.4454
SetCharge&DischargeRates | 0 | 0 | 0 | 0 | 0
FWH Split-2 | 0 | 0 | 0 | 0 | 0
Cond-charge cond 1/10 | 144300 | 285800 | 32800 | 60617 | 0
E-103 | 891000 | 1423700 | 247600 | 388358 | 0
SetTESHotStandbySaltFlowRate | 0 | 0 | 0 | 0 | 0
P-100 | 496900 | 1242000 | 30500 | 175368 | 34.689
C-IHX | 1848200 | 2895500 | 520200 | 807725 | 0
HotTank-2 | 4389400 | 7320300 | 0 | 849223 | 0
D-IHX | 600200 | 929000 | 164400 | 248308 | 0
CT | 7510600 | 11494000 | 0 | 1123530 | 0
Sized Diversion IHX-3 | 1609800 | 2892100 | 425600 | 728938 | 0
DischargeCond | 1325700 | 2308300 | 384300 | 583722 | 132.7499
CondModel | 8723800 | 17473800 | 2631200 | 4144354 | 0
RCY-2 | 0 | 0 | 0 | 0 | 0
BOP Pump | 90300 | 153800 | 4400 | 14976 | 11.563
BOP Pump-2 | 166900 | 278600 | 8400 | 26996 | 28.9075
D-IHX hot standby | 20900 | 115200 | 4100 | 23547 | 0
Condenser | 1444400 | 2455000 | 415200 | 618636 | 147.3239
FWH Mix-2 | 0 | 0 | 0 | 0 | 0
Sized SHX-3 | 1970400 | 3513100 | 537600 | 881410 | 0
SHX pump | 37600 | 251200 | 2400 | 49351 | 0.11547
Charging Calcs | 0 | 0 | 0 | 0 | 0
HotTank | 4389400 | 7320300 | 0 | 849223 | 0
ColdTank | 4307800 | 7142100 | 0 | 802159 | 0
ColdTank-2 | 4307800 | 7142100 | 0 | 802159 | 0
TES Pump-3 | 183000 | 437200 | 8800 | 59706 | 72.2687
Turbine | 3963600 | 4436900 | 219800 | 343017 | 0
Turbine-2 | 0 | 0 | 0 | 0 | 0
E-102 | 6728100 | 12877600 | 1900000 | 3129680 | 0
Calculations | 0 | 0 | 0 | 0 | 0
2ndBOPPump | 29700 | 86800 | 2000 | 10784 | 3.4689
DischargeCond-2 | 21400 | 100500 | 4300 | 16431 | 1.3507
IHX Pump | 9800 | 68400 | 540 | 11020 | 0.006975
BOP Ref Pump | 144800 | 240400 | 6800 | 20897 | 20.2353
TES Loop cond (sized 1/10) | 120700 | 232900 | 22800 | 43927 | 0
Condenser-2 | 1931500 | 3411500 | 564000 | 841895 | 268.045
K-101 | 0 | 0 | 0 | 0 | 0
DecoupledModelsSet | 0 | 0 | 0 | 0 | 0
Turbine-discharge (sized 1/3) | 2734600 | 3064400 | 146300 | 222587 | 0
C-IHX-2 | 89400 | 240600 | 22600 | 59812 | 0
2ndTurbine | 3034900 | 3386000 | 164000 | 247781 | 0
Steam Generator | 3268800 | 6402700 | 910000 | 1612730 | 0
2ndBOPPump-2 | 16300 | 42900 | 980 | 3245 | 0.0434
SPRDSHT-1 | 0 | 0 | 0 | 0 | 0
HT | 7677300 | 11808100 | 0 | 1192775 | 0
NPP Cond Ref Pump 1/10 | 8200 | 59100 | 570 | 8049 | 0.43323
FWH_Split | 0 | 0 | 0 | 0 | 0

## Equipment
Equipment
Name | Equipment Cost [USD] | Installed Cost [USD] | Equipment Weight [LBS] | Total Installed Weight [LBS] | Sizing Errors | Evaluation Errors
Steam Generator-2 | 3268800 | 6402700 | 910000 | 1612730
DisCond | 852500 | 1505000 | 249000 | 390226
1/10th NPP Ref Cond | 43700 | 129500 | 9000 | 23742
TES Loop cond pump (sized 1/10) | 17500 | 102100 | 1300 | 17739
TES Pump | 36600 | 247600 | 2400 | 47835
P-101 | 26700 | 73500 | 1700 | 7740
NPP Ref Turbine (1/3) | 2800200 | 3134600 | 150200 | 228104
2ndTurbine-2 | 52600 | 98300 | 3700 | 9658
NPP Ref Turbine | 0 | 0 | 0 | 0 |  | ERROR> 'TUR- 9' TURBINE POWER IS OUT OF RANGE
Cond-charge cond Pump 1/10 | 17300 | 101900 | 1300 | 17739
FWH_Mix | 0 | 0 | 0 | 0
SG | 3187100 | 6320600 | 883000 | 1585594
FWH Mix | 0 | 0 | 0 | 0
Discharging Calcs | 0 | 0 | 0 | 0
Turbine-charge (sized 1/2) | 2325800 | 2613600 | 122500 | 185589
NPP Ref Condenser | 0 | 0 | 0 | 0 |  | ERROR> 'HE - 16' DESIGN COULD NOT BE COMPLETED IN 50 SHELLS
FWH Split | 0 | 0 | 0 | 0
TES Pump-2 | 8000 | 54400 | 660 | 7266
FWH Split-2 | 0 | 0 | 0 | 0
Cond-charge cond 1/10 | 144300 | 285800 | 32800 | 60617
E-103 | 891000 | 1423700 | 247600 | 388358
P-100 | 496900 | 1242000 | 30500 | 175368
C-IHX | 1848200 | 2895500 | 520200 | 807725
HotTank-2 | 4389400 | 7320300 | 0 | 849223 |  | ERROR> 'VT - 24' PRESSURE IS OUT OF RANGE
D-IHX | 600200 | 929000 | 164400 | 248308
CT | 7510600 | 11494000 | 0 | 1123530 |  | ERROR> 'VT - 26' PRESSURE IS OUT OF RANGE
Sized Diversion IHX-3 | 1609800 | 2892100 | 425600 | 728938
DischargeCond | 1325700 | 2308300 | 384300 | 583722
CondModel | 8723800 | 17473800 | 2631200 | 4144354
RCY-2 | 0 | 0 | 0 | 0
BOP Pump | 90300 | 153800 | 4400 | 14976
BOP Pump-2 | 166900 | 278600 | 8400 | 26996
D-IHX hot standby | 20900 | 115200 | 4100 | 23547
Condenser | 1444400 | 2455000 | 415200 | 618636
FWH Mix-2 | 0 | 0 | 0 | 0
Sized SHX-3 | 1970400 | 3513100 | 537600 | 881410
SHX pump | 37600 | 251200 | 2400 | 49351
Charging Calcs | 0 | 0 | 0 | 0
HotTank | 4389400 | 7320300 | 0 | 849223 |  | ERROR> 'VT - 39' PRESSURE IS OUT OF RANGE
ColdTank | 4307800 | 7142100 | 0 | 802159 |  | ERROR> 'VT - 40' PRESSURE IS OUT OF RANGE
ColdTank-2 | 4307800 | 7142100 | 0 | 802159 |  | ERROR> 'VT - 41' PRESSURE IS OUT OF RANGE
TES Pump-3 | 183000 | 437200 | 8800 | 59706
Turbine | 3963600 | 4436900 | 219800 | 343017
Turbine-2 | 0 | 0 | 0 | 0 |  | ERROR> 'TUR- 44' TURBINE POWER IS OUT OF RANGE
E-102 | 6728100 | 12877600 | 1900000 | 3129680
Calculations | 0 | 0 | 0 | 0
2ndBOPPump | 29700 | 86800 | 2000 | 10784
DischargeCond-2 | 21400 | 100500 | 4300 | 16431
IHX Pump | 9800 | 68400 | 540 | 11020
BOP Ref Pump | 144800 | 240400 | 6800 | 20897
TES Loop cond (sized 1/10) | 120700 | 232900 | 22800 | 43927
Condenser-2 | 1931500 | 3411500 | 564000 | 841895
K-101 | 0 | 0 | 0 | 0 |  | ERROR> 'TUR- 53' DESIGN GAUGE PRESSURE OUTLET IS OUT OF RANGE ERROR> 'TUR- 53' POWER OUTPUT IS OUT OF RANGE
Turbine-discharge (sized 1/3) | 2734600 | 3064400 | 146300 | 222587
C-IHX-2 | 89400 | 240600 | 22600 | 59812
2ndTurbine | 3034900 | 3386000 | 164000 | 247781
Steam Generator | 3268800 | 6402700 | 910000 | 1612730
2ndBOPPump-2 | 16300 | 42900 | 980 | 3245
SPRDSHT-1 | 0 | 0 | 0 | 0
HT | 7677300 | 11808100 | 0 | 1192775 |  | ERROR> 'VT - 60' PRESSURE IS OUT OF RANGE
NPP Cond Ref Pump 1/10 | 8200 | 59100 | 570 | 8049
FWH_Split | 0 | 0 | 0 | 0

## TEMA HEX
TEMA HEX
User tag number | Steam Generator-2 | DisCond | 1/10th NPP Ref Cond | SG | NPP Ref Condenser | Cond-charge cond 1/10 | E-103 | C-IHX | D-IHX | Sized Diversion IHX-3 | DischargeCond | CondModel | D-IHX hot standby | Condenser | Sized SHX-3 | E-102 | DischargeCond-2 | TES Loop cond (sized 1/10) | Condenser-2 | C-IHX-2 | Steam Generator
Remarks 1 | Equipment mapped from 'Steam Generator-2'. | Equipment mapped from 'DisCond'. | Equipment mapped from '1/10th NPP Ref Cond'. | Equipment mapped from 'SG'. | Equipment mapped from 'NPP Ref Condenser'. | Equipment mapped from 'Cond-charge cond 1/10'. | Equipment mapped from 'E-103'. | Equipment mapped from 'C-IHX'. | Equipment mapped from 'D-IHX'. | Equipment mapped from 'Sized Diversion IHX-3'. | Equipment mapped from 'DischargeCond'. | Equipment mapped from 'CondModel'. | Equipment mapped from 'D-IHX hot standby'. | Equipment mapped from 'Condenser'. | Equipment mapped from 'Sized SHX-3'. | Equipment mapped from 'E-102'. | Equipment mapped from 'DischargeCond-2'. | Equipment mapped from 'TES Loop cond (sized 1/10)'. | Equipment mapped from 'Condenser-2'. | Equipment mapped from 'C-IHX-2'. | Equipment mapped from 'Steam Generator'.
Quoted cost per item [USD]
Currency unit for matl cost
Number of identical items | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Installation option
Heat transfer area [m2] | 13333.7114 | 5777.0833 | 131.607 | 13327.1137 | 118056.5178 | 719.9658 | 5469.4429 | 7222.5532 | 3272.6333 | 12391.33 | 8874.21 | 62782.2599 | 64.7972 | 9707.1757 | 16112.61 | 26048.13 | 66.5822 | 443.3683 | 13227.3686 | 311.348 | 13333.7114
Number of shells |  |  | 1 |  |  | 2 |  |  |  | 7 |  |  |  |  | 8 |  |  | 2
Front end TEMA symbol | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B
Shell TEMA symbol | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E
Rear end TEMA symbol | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M
Heat exchanger design option
Tube material |  |  | A 214 |  |  | A 214 |  |  |  | A 214 |  |  |  |  | A 214 |  |  | A 214
Tube design gauge pressure [kPag] | 3762.5061 | 415.7961 | 198.6711 | 3641.1584 | 415.7961 | 198.6711 | 680.2544 | 2393.8377 | 813.5877 | 198.6711 | 415.7961 | 243.4211 | 813.5877 | 415.7961 | 198.6711 | 2393.8377 | 415.7961 | 198.6711 | 415.7961 | 2393.8377 | 3762.5061
Tube design temperature [C] | 343.3333 | 121.1111 | 75 | 343.3333 | 121.1111 | 75 | 267.8006 | 334.6778 | 266.4787 | 345 | 121.1111 | 121.1111 | 267.786 | 121.1111 | 255 | 334.6778 | 121.1111 | 75 | 121.1111 | 334.6778 | 343.3333
Tube operating temperature [C] | 306.9 | 35 | 41.6761 | 306.8889 | 35 | 41.6761 | 240.0228 | 238.6907 | 238.701 | 238.3283 | 35 | 37.8737 | 240.0082 | 35 | 238.7 | 240.0228 | 35 | 41.67 | 35 | 240 | 306.9
Tube outside diameter [m] | 0.0254 | 0.0254 | 0.01905 | 0.0254 | 0.0254 | 0.01905 | 0.0254 | 0.0254 | 0.0254 | 0.01905 | 0.0254 | 0.0254 | 0.0254 | 0.0254 | 0.01905 | 0.0254 | 0.0254 | 0.01905 | 0.0254 | 0.0254 | 0.0254
Shell material |  |  | A 516 |  |  | A 516 |  |  |  | A 516 |  |  |  |  | A 516 |  |  | A 516
Shell design gauge pressure [kPag] | 2474.5611 | 243.4211 | 198.6711 | 2393.6626 | 243.4211 | 198.6711 | 1071.0461 | 3641.4211 | 1271.0461 | 3698.6711 | 243.4211 | 128.5044 | 1271.0461 | 243.4211 | 1298.6711 | 3641.4211 | 243.4211 | 198.6711 | 243.4211 | 3641.4211 | 2474.5611
Shell design temperature [C] | 343.3333 | 121.1111 | 80 | 343.3333 | 121.1111 | 80 | 262.7778 | 334.6778 | 245.7778 | 275 | 121.1111 | 121.1111 | 262.7778 | 121.1111 | 275 | 334.6778 | 121.1111 | 80 | 121.1111 | 334.6778 | 343.3333
Shell operating temperature [C] | 315.5556 | 41.5188 | 37.8737 | 315.5556 | 41.6763 | 38.1706 | 235 | 306.9 | 218 | 306.9 | 41.6748 | 41.6761 | 235 | 41.6753 | 219.8305 | 306.9 | 41.6741 | 36.6271 | 41.6761 | 306.9 | 315.5556
Tube side pipe material
Shell side pipe material
Number of tubes per shell |  |  | 757 |  |  | 1726 |  |  |  | 5113 |  |  |  |  | 6089 |  |  | 1520
Tube length extended [m] | 6.096 | 6.096 | 3 | 6.096 | 6.096 | 3.6 | 6.096 | 6.096 | 6.096 | 6 | 6.096 | 6.096 | 6.096 | 6.096 | 5.7 | 6.096 | 6.096 | 2.55 | 6.096 | 6.096 | 6.096
Tube gauge
Tube pitch [m] | 0.03175 | 0.03175 | 0.023813 | 0.03175 | 0.03175 | 0.023813 | 0.03175 | 0.03175 | 0.03175 | 0.023813 | 0.03175 | 0.03175 | 0.03175 | 0.03175 | 0.023813 | 0.03175 | 0.03175 | 0.023813 | 0.03175 | 0.03175 | 0.03175
Shell diameter [m] |  |  | 0.73905 |  |  | 0.73905 |  |  |  | 0.73905 |  |  |  |  | 0.73905 |  |  | 0.73905
Shell wall thickness [m]
Shell corrosion allowance [m] |  |  | 0.003175 |  |  | 0.003175 |  |  |  | 0.003175 |  |  |  |  | 0.003175 |  |  | 0.003175
Expansion joint
Tube sheet material
Number of tube passes | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Number of shell passes | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Allow resize

## Centrif pump
Centrif pump
User tag number | TES Loop cond pump (sized 1/10) | TES Pump | P-101 | Cond-charge cond Pump 1/10 | TES Pump-2 | P-100 | BOP Pump | BOP Pump-2 | SHX pump | TES Pump-3 | 2ndBOPPump | IHX Pump | BOP Ref Pump | 2ndBOPPump-2 | NPP Cond Ref Pump 1/10
Remarks 1 | Equipment mapped from 'TES Loop cond pump (sized 1/10)'. | Equipment mapped from 'TES Pump'. | Equipment mapped from 'P-101'. | Equipment mapped from 'Cond-charge cond Pump 1/10'. | Equipment mapped from 'TES Pump-2'. | Equipment mapped from 'P-100'. | Equipment mapped from 'BOP Pump'. | Equipment mapped from 'BOP Pump-2'. | Equipment mapped from 'SHX pump'. | Equipment mapped from 'TES Pump-3'. | Equipment mapped from '2ndBOPPump'. | Equipment mapped from 'IHX Pump'. | Equipment mapped from 'BOP Ref Pump'. | Equipment mapped from '2ndBOPPump-2'. | Equipment mapped from 'NPP Cond Ref Pump 1/10'.
Quoted cost per item [USD]
Currency unit for matl cost
Number of identical items
Installation option
Casing material
Liquid flow rate [m3/h] | 516.1609 | 1859.6236 | 91.4524 | 488.3679 | 37.1963 | 9326.6357 | 121.0491 | 222.9197 | 1901.6251 | 1859.6236 | 106.8892 | 152.3234 | 218.9892 | 1.0863 | 93.2664
Fluid head [m] | 12.9312 | 0.031453 | 102.1632 | 12.9215 |  | 12.9215 | 361.1304 | 546.9917 | 0.11793 |  | 122.7239 | 0.11722 | 359.9215 | 122.7606 | 12.9215
Speed [rpm]
Fluid specific gravity | 0.99658 | 1.948 | 0.99154 | 0.99658 | 1.948 | 0.99658 | 0.9933 | 0.99148 | 1.905 | 1.948 | 0.99336 | 0.87113 | 0.99641 | 0.99154 | 0.99658
Driver power [kW]
Driver type
Seal type
Design gauge pressure [kPag] | 243.4211 | 243.4211 | 1071.0461 | 243.4211 | 243.4211 | 243.4211 | 3762.4211 | 5562.4211 | 243.4211 | 243.4211 | 1271.0461 | 3641.4211 | 3762.4211 | 1271.0461 | 243.4211
Design temperature [C] | 121.1111 | 207.7778 | 121.1111 | 121.1111 | 207.7778 | 121.1111 | 121.1111 | 121.1111 | 266.4787 | 207.7778 | 121.1111 | 223.478 | 121.1111 | 121.1111 | 121.1111
Fluid viscosity [cP] | 0.858 | 11.194 | 0.635 | 0.858 | 11.194 | 0.858 | 0.694 | 0.633 | 6.049 | 11.194 | 0.696 | 0.138 | 0.849 | 0.635 | 0.858
Pump efficiency [%] | 75 | 90 | 75 | 75 | 90 | 75 | 90 | 90 | 90 | 90 | 90 | 75 | 90 | 90 | 75
Allow resize

## Condensing turbine
Condensing turbine
User tag number | NPP Ref Turbine (1/3) | 2ndTurbine-2 | NPP Ref Turbine | Turbine-charge (sized 1/2) | Turbine | Turbine-2 | Turbine-discharge (sized 1/3) | 2ndTurbine
Remarks 1 | Equipment mapped from 'NPP Ref Turbine (1/3)'. | Equipment mapped from '2ndTurbine-2'. | Equipment mapped from 'NPP Ref Turbine'. | Equipment mapped from 'Turbine-charge (sized 1/2)'. | Equipment mapped from 'Turbine'. | Equipment mapped from 'Turbine-2'. | Equipment mapped from 'Turbine-discharge (sized 1/3)'. | Equipment mapped from '2ndTurbine'.
Quoted cost per item [USD]
Currency unit for matl cost
Number of identical items
Installation option
Material
Power output [kW] | 16697.1912 | 192.0996 | 49031.6449 | 13064.0693 | 26431.2556 | 48585.8031 | 16181.5208 | 18571.8241
Steam gauge pressure [kPag]
Speed [rpm]
Allow resize

## Quoted equipment
Quoted equipment
User tag number | FWH_Mix | FWH Mix | Discharging Calcs | FWH Split | FWH Split-2 | RCY-2 | FWH Mix-2 | Charging Calcs | Calculations | SPRDSHT-1 | FWH_Split
Remarks 1 | Equipment mapped from 'FWH_Mix'. | Equipment mapped from 'FWH Mix'. | Equipment mapped from 'Discharging Calcs'. | Equipment mapped from 'FWH Split'. | Equipment mapped from 'FWH Split-2'. | Equipment mapped from 'RCY-2'. | Equipment mapped from 'FWH Mix-2'. | Equipment mapped from 'Charging Calcs'. | Equipment mapped from 'Calculations'. | Equipment mapped from 'SPRDSHT-1'. | Equipment mapped from 'FWH_Split'.
Code of account | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Icarus/User COA option
Material cost per unit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Currency unit for matl cost
Labor hours per unit [hours]
Number of identical items
Installation option
Unit of measure
Quantity
Quantity adjustment option
Item classification
Item type
Material
Component weight [kg]
ID in bulk report
Allow resize

## Storage tank
Storage tank
User tag number | HotTank-2 | CT | HotTank | ColdTank | ColdTank-2 | HT
Remarks 1 | Equipment mapped from 'HotTank-2'. | Equipment mapped from 'CT'. | Equipment mapped from 'HotTank'. | Equipment mapped from 'ColdTank'. | Equipment mapped from 'ColdTank-2'. | Equipment mapped from 'HT'.
Quoted cost per item [USD]
Currency unit for matl cost
Number of identical items
Installation option
Shell material
Volume units | GALLONS | GALLONS | GALLONS | GALLONS | GALLONS | GALLONS
Liquid volume(Gallon/Barrel/M3)
Vessel diameter [m] | 49.2252 | 57.912 | 49.2252 | 48.9204 | 48.9204 | 58.3692
Vessel height [m] | 23.0124 | 27.2796 | 23.0124 | 22.86 | 22.86 | 27.432
Roof type
Bottom type
Design gauge pressure [kPag] | 243.4211 | 243.4211 | 243.4211 | 243.4211 | 243.4211 | 243.4211
Design temperature [C] | 266.4778 | 207.7778 | 266.4684 | 207.7778 | 207.7778 | 267.8006
Operating temperature [C]
Base material thickness [m]
Corrosion allowance [m]
Cladding material
Cladding thickness [m]
Fluid specific gravity
Allow resize

## Turboexpander
Turboexpander
User tag number | K-101
Remarks 1 | Equipment mapped from 'K-101'.
Quoted cost per item [USD]
Currency unit for matl cost
Number of identical items
Installation option
Actual gas flow rate Inlet [ACT_m3/h] | 20387.9966
Design gauge pressure Inlet [kPag] | 898.6711
Design temperature Inlet [C] | 235
Design gauge pressure Outlet [kPag] | -93.3289
Power output [kW] | 15739.2328
Molecular weight | 18.0151
Specific heat ratio | 1.258
Compressibility factor Inlet | 0.95868
Isentropic efficiency [%] | 90
Number of spare cartridges
Allow resize